## Slide 1
Achieving an 80% Renewable Portfolio in Alaska’s Railbelt: Cost Analysis
Presentation to the Alaska State Legislature House Labor and Commerce Committee
Paul Denholm, Marty Schwarz, Lauren Streitmatter
April 3, 2024

## Slide 2
Brookhaven Laboratory
Oak Ridge National Laboratory
Savannah River National Laboratory
Ames Laboratory
Argonne National Laboratory
National Renewable Energy Laboratory
Pacific Northwest National Laboratory
Idaho National Laboratory
Los Alamos National Laboratory
Sandia National Laboratories
Lawrence Berkeley National Laboratory
SLAC National Accelerator Laboratory
Lawrence Livermore National Laboratory
Sandia National Laboratories
Princeton Plasma Physics Laboratory
Jefferson Lab
Fermilab
National Energy Technology Laboratory
National Energy Technology Laboratory
NREL’s Fairbanks Campus
Alaska
NREL and the National Lab System
The 17 national laboratories have served as the leading institutions for scientific innovation in the United States for more than 90 years.
Hawaii

## Slide 3
Overview of study

## Slide 4: Scope of Study – The Alaska Railbelt
About 75% of state’s electricity demand
Average Railbelt residential electricity cost in 2022 was about 23 cents/kWh. U.S. average was about 14 cents/kWh.
Utility | Annual Sales (GWh) | Customer Accounts (thousands) | Fraction of Railbelt Annual Demand (%)
Chugach Electric Association | 1,903 | 113 | 43
Golden Valley Electric Association | 1,244 | 48 | 28
Matanuska Electric Association | 766 | 69 | 17
Homer Electric Association | 453 | 33 | 10
City of Seward Electric Department | 53 | 3 | 1
Total | 4,404 | 266 | 100

## Slide 5: The Challenge – Potential Increase in Costs
Natural gas prices expected to increase by more than 30% due to need for liquified natural gas (LNG) imports
Technology | Capacity (MW) | Energy (GWh) | Generation Fraction
Natural gas | 1,332.6 | 3,052 | 64%
Coal | 117.5 | 545 | 11%
Oil | 268.9 | 444 | 9%
Hydropower | 189.8 | 578 | 12%
Wind | 44.5 | 107 | 2%
Landfill gas | 11.5 | 41 | 1%
Total | 1,965 | 4,766 | 100%
Natural gas and oil provided >70% of Railbelt Generation in 2022
This will raise Railbelt electricity costs by about $75M/yr by 2029

## Slide 6: A Key Point of Comparison - Avoided Generation Cost
Can renewable energy offset the fuel use at existing plants at a lower cost?

## Slide 7: The Main Question
Can the addition of renewable energy reduce costs for Railbelt electricity consumers while maintaining existing levels of reliability?

## Slide 8: Study Framework– Compare Differences in Costs Associated with Deploying Renewable Energy
New Fossil Fixed and Variable Costs
Existing Fossil Generator Fuel and Variable Costs
Reference Case
RPS Case
New Fossil Fixed and Variable Costs
Existing Fossil Generator Fuel and Variable Costs
Existing Debt and PPA Obligations
Distribution System Costs
New Renewable and Storage Costs
Common New Capital and Fixed Costs (Generation, Transmission, and Storage)
Costs not considered in this study
Costs considered in this study
$
Renewable Costs Include:
Capital
Operations and Maintenance
Interconnection
Transmission spur line and interconnection
Additional natural gas storage
Grid-forming inverters
Additional operating reserves
Scheduling, forecasting, and communication
Curtailed energy
New Renewable and Storage Costs
Fossil Generator Costs Include:
Reduction in efficiency from operating at part load
Additional stops and starts
Notes: Our best guess - based on contract prices and other limited data - is that is a very high RPS is probably lower cost than a fossil-only scenario. (But likely only a subset of the scenarios evaluated).
It would take several weeks to do the detailed engineering analysis for the costs with the level of confidence needed to put that in writing.

## Slide 9: Modeling Approach – Follows Standard Integrated Resource Planning Process
Capacity Expansion model to determine cost-optimal mix of resources
Production cost modeling to validate load balance and operating reserves

## Slide 10: Analysis Framework
Three reliability zones. MEA/CEA combined into “central zone”
We assume resources are planned and dispatched in a coordinated manner
But we do not assume consolidated utilities.

## Slide 11: Scenarios
No New RE – only existing renewables, new fossil allowed
Reference – all generation resources allowed
Reference with RE cost +20% and -10%
RPS - meet the 80% by 2040 RPS
  Eligible technologies based on SB 101: wind, solar, geothermal, tidal, hydropower, biomass, and landfill gas, and include both existing and new deployments
Year | Value
2027 | 25%
2035 | 55%
2040 | 80%

## Slide 12: Generation Options
Technology | Notes
Fossil | 
Coal and Gas Cogeneration | Not considered with exceptions noted
Conventional Coal | Existing and new
Natural Gas Combined Cycle (CCGT) | Existing and new
Natural Gas Combustion Turbine | Existing and new
Oil/Gas Internal Combustion Engine | Only existing capacity.
Oil/gas steam | Only existing capacity
Renewables | 
Biomass (solid biomass combustion) | No (preliminary analysis indicated this would be uncompetitive)
Geothermal | New capacity at a single location after 2034
Hydropower | Existing plants plus new run-of-river. No new large conventional hydropower.
Landfill Gas | Only existing capacity
Land-Based Wind | Existing and new (only utility scale)
Offshore Wind | New capacity after 2030 in the Cook Inlet
Rooftop PV | Only existing capacity in base scenario. Prescribed builds as a sensitivity.
Tidal | No
Utility-Scale PV | Existing and New
Storage | 
Battery Storage | Existing and new
Pumped Storage Hydro | No

## Slide 13: Load Growth
Scaled based on projected population growth (about 4%) by 2040
Electric vehicle adoption values from ACEP, about 20% of vehicles by 2040 – adds abound additional 16% growth in electricity demand

## Slide 14: Transmission & Interconnection
AK Intertie – 78 MW of available transfer capacity. No upgrades.
Kenai intertie – 75 MW. Upgraded to 185 MW in 2033 in all scenarios as part of the Railbelt Innovative Resiliency Project.
Solar and PV interconnections are added as needed and optimized by the model (assumed eligible for ITC).

## Slide 15
Cost and Performance of New Renewable Resources

## Slide 16: Costs of Acquiring New Renewables
Capital cost
Fixed O&M
Interconnection
Transmission spur lines
Integration costs
Captured in a power purchase agreement

## Slide 17: New RE Financing Assumptions
All dollars in $2023 unless otherwise specified
We use NREL ATB mid-case inputs
25 yr finance period
Can be obtained via PPA or utility developed.
40% ITC based on the assumption that all of the Railbelt qualifies as an energy community
There are several external efforts underway to get Anchorage to qualify for the ITC bonus.

## Slide 18: Alaska Renewable Cost Multiplier
Decline in multiplier based on maturing market place

## Slide 19: Renewable Capital Cost
Added GFM inverters.
Costs shown are before spur line, substation upgrade and fuel storage costs

## Slide 20: Wind Generation Cost
Assumes a 37% CF

## Slide 21: Wind Sites Evaluated

## Slide 22: Both wind and PV can be developed below the avoided cost of natural gas

## Slide 23: Integration Costs Considered
Spur lines and interconnection
Additional thermal plant start costs and part-load operation
Operating reserve requirements
Natural gas fuel storage requirements
Renewable forecasting and communications cost
Cost of grid forming inverters

## Slide 24: Reliability Benefits of Renewables?
We assume the are essentially zero – we do not allow wind and solar energy to provide substantial reliability benefits.
The only benefits of wind and solar accounted for is their ability to offset natural gas and other use AFTER taking into account costs of integrating them on the Railbelt grid.

## Slide 25
Results (Key Findings)

## Slide 26: Finding #1: The Least-Cost (Reference) Scenario Results in Substantial Deployment of Renewable Energy and Cost Savings
Reference case hits 76% renewables in 2040.

## Slide 27: Annual Costs of No New RE and Reference Scenarios
Doesn’t include common costs
Net savings reach about $100M/yr by the mid 2030s
Annual net savings shown in the black lines. Negative values are the costs, positive values are the savings.

## Slide 28: Cumulative Savings of the Reference Scenario (2024-2040) Exceeds $1 Billion (Undiscounted)
By 2040 renewable deployment has avoided about $4.2 Billion in cumulative fuel and other costs. This requires investments of about $2.9 Billion in renewables and other infrastructure directly related to renewables integration

## Slide 29: Finding #2: The Least-Cost (Reference) Scenario Relies on a Mix of Renewable Energy Resources and Locations
Existing fossil resources maintained for reliability purposes (Finding #4)
About 50% annual electricity from wind in 2040

## Slide 30: Installed Capacity
Wind is deployed in all three locations, but highest quality resources are in GVEA and HEA zones.
Wind deployment in HEA zone takes advantage of transmission upgrades as part of the Railbelt Innovative Resiliency Project.
Solar deployment is largely in central, due in part to limited wind resources and proximity to load centers.

## Slide 31: Finding #3: The 80% RPS Has Limited Impact on Costs
Requiring an 80% RPS reduces the net savings by about $19 million in 2040, which is less than a 2% change in cumulative savings. Differences are very small given the large uncertainty in future costs of fuels and renewable generation. This is demonstrated by the much larger impact that a change in the assumed cost of renewable energy shown in the high- and low-cost RE sensitivities.
Impact of 80% RPS requirement occurs mostly in 2040.

## Slide 32: Finding #4: Demand Is Met in All Scenarios, Relying Heavily on Existing Hydro and Fossil-Fueled Generators During Periods of Low Renewable Output

## Slide 33
Finding #5: Large Contributions of Renewable Generation Will Require Substantial Changes to How the System Is Operated
Hourly fraction of generation met by wind and solar

## Slide 34: Finding #5: Large Contributions of Renewable Generation Will Require Substantial Changes to How the System Is Operated
Large swings in renewable output and large variation in hydropower and thermal plants

## Slide 35
Finding #6: Cost Impacts of Addressing Variability and Uncertainty Are Modest Relative to Savings But With Remaining Uncertainties
Cost of renewable purchases ($284M in 2040)
Cost of renewable integration and addressing variability ($44M in 2040)
Net savings ($121M in 2040)

## Slide 36: Conclusions
New renewable energy has potentially lower cost than variable cost of existing natural gas fueled generators
Large opportunity to stabilize electricity prices and reduce impact of increased natural gas costs
There are considerable uncertainties and additional analysis needed
  Stability analysis – will grid forming inverters be sufficient? (Addressing via synchronous machines could reduce benefits by ~10%)
  There is large uncertainty about the costs of renewable development in Alaska
  We did not consider new hydropower options
  Impact of changes in natural gas consumption for electricity on supply and costs for heating

## Slide 37
Thank you
Full Report at https://www.nrel.gov/docs/fy24osti/85879.pdf

## Slide 38
Backup slides

## Slide 39: Example of start cost difference
About $3M/yr in additional start costs in the 2030s – $29M from 2024-2040

## Slide 40: Considerable uncertainty about required fuel storage costs
We add about 40 million standard cubic feet of storage in the Reference Scenario by 2040 reaching about $9.5 million/year in additional costs.
Additional considerations of deliverability are needed

## Slide 41: Increased Ramping and Part-Load Operation of Thermal Plants
Wind and solar output drops by over 570 MW over the day
Fossil generation increases by 300 MW over a 5-hour period in the afternoon

## Slide 42: Increased Ramping and Part-Load Operation of Thermal Plants
2022 Actual

## Slide 43: Potential Changes in Hydropower Plant and Transmission Operation
Flow on the Alaska Intertie (black) in 2040 in the Reference scenario depends largely on the supply of wind (orange) in the GVEA region. Positive numbers represent a flow from GVEA to Central.
Operation of the Bradley Lake hydropower plant during periods of highly variable renewable output

## Slide 44: Potential Changes in Transmission Operation
HEA to Central
GVEA to Central

## Slide 45: Renewables Dispatch for Balancing Load and for Reserve Provision
Total upward operating reserves required (top) in the No New RE and Reference cases. Total requirement is the black bar. Reserves requirement by type for the Reference case is shown in the bottom. Down reserves are not shown.

## Slide 46: Decline in economic deployment of wind/solar is largely due to increased curtailment
Marginal curtailment is about 50%

## Slide 47: 2040 Mix of Resources
Technology Type | No New RE |  |  | Reference |  | 
 | Capacity (MW) | Annual Energy (GWh) | Annual Energy (%) | Capacity (MW) | Annual Energy (GWh) | Annual Energy (%)
Fossil | 1,673 | 5,100 | 86% | 1,473 | 1,442 | 24%
Land-Based Wind | 43 | 76 | 1% | 1,400 | 3,058 | 51%
Solar | 34 | 42 | 1% | 577 | 776 | 13%
Hydropower | 179 | 653 | 11% | 179 | 629 | 11%
Other Renewables | 7 | 55 | 1% | 7 | 36 | 1%
Storage (net generation) | 133 | 20 (-4) |  | 270 | 102 (-19) | 
Total | 2,068 | 5,926 | 100% | 3,905 | 5,941 | 100%
[1] Generation values are after removing curtailment (which must still be paid for). Curtailment of generators is based on marginal cost. For plants with zero generation cost (wind and solar), plants taking the ITC will be curtailed before those taking the PTC.

## Slide 48: Joint Dispatch & Planning
We assume resources are planned and dispatched in a coordinated manner
But we do not assume consolidated utilities or a single BA that co-optimizes energy and reserves.
  Planning reserves held in individual zones
  Operating reserves (contingency, regulation, and flexible ramping) held in individual zones and cannot be shared
  Interconnections cannot be used for the purposes of providing operating reserves or peak capacity

## Slide 49: Reliability Requirements
30% planning reserve margin in each zone
Cannot use interties for planning reserves (all resources must be in the same zone to count towards planning reserves)
Synchronized contingency reserve of 80 MW
Load regulation reserve 2% of load in HEA, Central and 5% of load in GVEA (each zone, not shared)

## Slide 50: Load Shapes
Profiles use 2018 weather conditions
Winter peak generation for three modeled utility regions: Central, GVEA, and HEA
Total generation in three periods in Alaska’s Railbelt

## Slide 51: Load Growth
Scaled based on projected population growth (about 4%) by 2040
Region | Generation Requirement |  | Total Increase (%)
 | 2024 | 2040 | 
Central | 2,972 | 3,132 | 5.4%
Golden Valley Electric Association | 1,242 | 1,264 | 1.8%
Homer Electric Association | 473 | 464 | -1.8%
Total | 4,686 | 4,860 | 3.7%
Assumed Load Growth Based on Population (Before Addition of Electric Vehicles)

## Slide 52: Electric Vehicles
Projections, profiles from ACEP
Most conservative projection used
20% of all vehicles by 2040 (110,000)
782 GWh additional load

## Slide 53: Prescribed changes from base generation mix
Only retirement is Healy Unit 2
Add 86 MW of new batteries
Technology | Capacity (MW) | Energy (GWh) | Generation Fraction
Natural gas | 1,332.6 | 3,052 | 64%
Coal | 117.5 | 545 | 11%
Oil | 268.9 | 444 | 9%
Hydropower | 189.8 | 578 | 12%
Wind | 44.5 | 107 | 2%
Landfill gas | 11.5 | 41 | 1%
Total | 1,965 | 4,766 | 100%
Base 2022 generation mix

## Slide 54: Wind Cost Supply Curve
Includes spur line, but not substation upgrades or fuel storage calculated separately

## Slide 55: Cost Sensitivity
Wind now starts at about twice the cost of the L48 and solar is substantially more expensive than what has already been deployed in Alaska